**Fire Watch Procedures**

Interruption of normal operation of a fire protection system for any purpose constitutes a “temporary shutdown.” Types of interruptions include, but are not limited to, periodic inspection or testing, maintenance, and repairs. During a shutdown, alternative measures are necessary to ensure that the level of safety intended by the code is maintained.

In the event any building fire protection system is shut down or impaired for any reason whatsoever, a Fire Watch through the use of Fire Watch personnel is to be implemented immediately. During a Fire Watch, a responsible occupant, employee or contracted security guard actively looks for evidence of smoke and fire, listens for in-room smoke detectors sounding and, if smoke or fire is found, they are to contact 911 and alert building occupants to the fire.

The Fire Watch is only intended as a short-term alternative that permits continued occupancy of the building. The Winkler Fire Depart requires the immediate action of the building owner, business operator or management firm to arrange for permanent corrective measures to be taken on the particular system which is temporarily out of service. Alternative measures for the temporary shutdown of the building’s fire protection systems are to be outlined within the Fire Safety Plan for the building.

Definition: The term “Fire Watch” is used to describe a dedicated trained person or persons whose sole responsibility is to look for fires within an established area; this could be a responsible occupant, employee or contracted security guard.

1. At least one 1 qualified person shall be employed to complete fire watch duties of the unprotected building area 24 hours per day.
2. If a fire alarm and detection system or part thereof, is inoperative for any reason the Winkler Fire Department must be notified by calling 204-325-8151 and emailing the filled out Fire Watch Advisement form to **info@winklerfire.com** .
3. Fire Watch personnel are to post signage throughout the common areas of the building indicating what fire protection system is temporarily out of order and display the emergency evacuation procedures, as outlined within the approved Fire Safety Plan.
4. Each person assigned to Fire Watch duties should be provided with the following equipment:
	1. Suitable means of communication for notifying 911
	2. A portable air horn, whistle or other suitable means of sounding an alarm to notify building occupants
	3. Copy of the Fire Watch Log Sheet
	4. Keys and/or access codes to provide entry to all rooms/spaces
	5. Floor plan of the building under Fire Watch (if available) Winkler Fire department
5. Fire Watch personnel must tour the entire building each hour and document this on the Fire Watch Log Sheet. The person completing the rounds will record the time each round was completed and sign or initial each entry.
6. Fire watch personnel must be familiar with the location of portable fire extinguishers in the building and be trained in their use.
7. If fire or smoke conditions are discovered:
	1. Alert building occupants.
	2. Call 911 from a safe area to report fire.
	3. Attempt to fight small fires only if it is safe to do so.
	4. Provide assistance to occupants in evacuating.
8. “Hot works” such as welding or cutting shall be prohibited in the area where the sprinkler protection is impaired or be limited to areas where approved precautions have been put into place.
9. Exit doors, access to exits and corridors are to be checked periodically for proper operation and obstructions while performing Fire Watch duties.
10. Cancelling the fire watch is based on an assessment that the fire protection system(s) is fully operational – at which time Winkler Fire Department must then be notified by calling 204-325-8151. If your fire protection system is monitored, you will also need to notify your monitoring station.

**Fire Watch Advisement Form**

**The Winkler Fire Department Fire Watch Procedures and the Building Fire Safety Plan should be reviewed at the implementation of fire watch. These records must be kept on site for a minimum of 2 years and be made available upon the request of Winkler Fire Department personnel.**

**Additional copies of this form can be downloaded from** [**https://www.winklerfire.com/**](https://www.winklerfire.com/)

**This form should be filled out and sent to the Winkler Fire Department** **info@winklerfire.com**

**\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_System OUT OF SERVICE Date: \_\_\_\_\_\_\_\_\_\_\_ Time: \_\_\_\_\_\_\_\_\_\_**

**Notify Winkler Fire Department – System Out of Service Date: \_\_\_\_\_\_\_\_\_\_\_ Time: \_\_\_\_\_\_\_\_\_**

**Notification to Monitoring Agency – System Out of Service Date: \_\_\_\_\_\_\_\_\_\_\_ Time: \_\_\_\_\_\_\_\_\_**

**\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_System BACK IN SERVICE Date: \_\_\_\_\_\_\_\_\_\_\_ Time: \_\_\_\_\_\_\_\_\_\_**

**Notify Winkler Fire Department - System Back in Service Date: \_\_\_\_\_\_\_\_\_\_\_ Time: \_\_\_\_\_\_\_\_\_**

**Notification to Monitoring Agency – System Back in Service Date: \_\_\_\_\_\_\_\_\_\_\_ Time: \_\_\_\_\_\_\_\_\_**

**NAMES & POSITIONS OF PERSONS CONDUCTING FIRE WATCH: INITIALS**

|  |  |  |
| --- | --- | --- |
| **Name** | **Position** | **Initials**  |
|  |  |  |
|  |  |  |
|  |  |  |
|  |  |  |

**FIRE WATCH LOG SHEET**

**NOTE: start a new Fire Watch Log Sheet for each new day of Fire Watch**

**Fire Watch Commenced: Date:\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_ Time:\_\_\_\_\_\_\_\_\_\_\_\_\_\_**

|  |  |  |  |
| --- | --- | --- | --- |
| **Rounds** | **Inspection time** | **Areas patrolled** | **Initials** |
| **1** | **a.m.****p.m.** |  |  |
| **2** | **a.m.****p.m.** |  |  |
| **3** | **a.m.****p.m.** |  |  |
| **4** | **a.m.****p.m.** |  |  |
| **5** | **a.m.****p.m.** |  |  |
| **6** | **a.m.****p.m.** |  |  |
| **7** | **a.m.****p.m.** |  |  |
| **8** | **a.m.****p.m.** |  |  |
| **9** | **a.m.****p.m.** |  |  |
| **10** | **a.m.****p.m.** |  |  |
| **11** | **a.m.****p.m.** |  |  |
| **12** | **a.m.****p.m.** |  |  |
| **13** | **a.m.****p.m.** |  |  |
| **14** | **a.m.****p.m.** |  |  |
| **15** | **a.m.****p.m.** |  |  |

**OUT OF SERVICE SIGNAGE**

**INSTRUCTIONS:**  Note what fire protection system is out of service and post copies of this sign at main entrance and on all floor areas

\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_\_

**(Fire protection system out of service)**

**OUT OF SERVICE**

**A FIRE WATCH IS PATROLLING THE AFFECTED AREAS OF THE BUILDING**

**IN CASE OF FIRE CALL 911 FOLLOW POSTED EMERGENCY PROCEDURES**